## signals-template-type-12
Signals IO List Template Type | 12
Name | Description | Signal Type | Fieldbus | Comm Protocol | Hardware Platform | Group
R001_FIT_113_wInValue | Flow transmitter for measuring primary cooling water flow in main loop | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PIT_114_wInValue | Pressure transmitter for cooling water pressure upstream cooled objects | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PIT_118_wInValue | Pressure transmitter measuring pressure after cooled objects | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PSZ_101_bInInput | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PSZ_102_bInInput | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PSZ_103_bInInput | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_PSZ_104_bInInput | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_QIT_112_wInValue | Conductivity transmitter for conductivity measurement in main cooling loop | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_001_bInSignalContactor | Frequency converter controlling pump R001-P-001 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_001_wInSpeedAct | Frequency converter controlling pump R001-P-001 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_001_bInMotorProtector | Frequency converter controlling pump R001-P-001 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_001_bInLocalDisconnect | Frequency converter controlling pump R001-P-001 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_001_wOutSpeedSetpoint | Frequency converter controlling pump R001-P-001 | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_001_bOutContactor | Frequency converter controlling pump R001-P-001 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_002_bInSignalContactor | Frequency converter controlling pump R001-P-002 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_002_wInSpeedAct | Frequency converter controlling pump R001-P-002 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_002_bInMotorProtector | Frequency converter controlling pump R001-P-002 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_002_bInLocalDisconnect | Frequency converter controlling pump R001-P-002 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_002_wOutSpeedSetpoint | Frequency converter controlling pump R001-P-002 | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_SICA_002_bOutContactor | Frequency converter controlling pump R001-P-002 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R001_TT_109_wInValue | Primary cooling water temperature downstream R001-W-001 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_FIT_113_wInValue | Flow transmitter for measuring primary cooling water flow in main loop | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_PIT_114_wInValue | Pressure transmitter for cooling water pressure upstream cooled objects | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_PIT_118_wInValue | Pressure transmitter measuring pressure after cooled objects | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_PSZ_101_bInInput | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_PSZ_102_bInInput | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_QIT_112_wInValue | Conductivity transmitter for conductivity measurement in main cooling loop | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_005_bInSignalContactor | Frequency converter controlling pump R002-P-005 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_005_wInSpeedAct | Frequency converter controlling pump R002-P-005 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_005_bInMotorProtector | Frequency converter controlling pump R002-P-005 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_005_bInLocalDisconnect | Frequency converter controlling pump R002-P-005 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_005_wOutSpeedSetpoint | Frequency converter controlling pump R002-P-005 | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_005_bOutContactor | Frequency converter controlling pump R002-P-005 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_006_bInSignalContactor | Frequency converter controlling pump R002-P-006 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_006_wInSpeedAct | Frequency converter controlling pump R002-P-006 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_006_bInMotorProtector | Frequency converter controlling pump R002-P-006 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_006_bInLocalDisconnect | Frequency converter controlling pump R002-P-006 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_006_wOutSpeedSetpoint | Frequency converter controlling pump R002-P-006 | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_SICA_006_bOutContactor | Frequency converter controlling pump R002-P-006 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R002_TT_109_wInValue | Primary cooling water temperature downstream R002-W-003 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_FCV_110_wOutCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PDT_106_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow to reactors primary cooling | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PDT_107_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow to convertors primary cooling | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PDT_110_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PDT_115_wInValue | Differential pressure transmitter for measuring ext. supply cooling water flow | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PDT_120_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow to nitrogen gas treatment | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_PT_104_wInValue | Pressure transmitter measuring supply pressure to cooled objects | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_SICA_104_bInSignalContactor | Frequency converter controlling pump R004-P-007 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_SICA_104_wInSpeedAct | Frequency converter controlling pump R004-P-007 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_SICA_104_bInMotorProtector | Frequency converter controlling pump R004-P-007 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_SICA_104_bInLocalDisconnect | Frequency converter controlling pump R004-P-007 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_SICA_104_wOutSpeedSetpoint | Frequency converter controlling pump R004-P-007 | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_SICA_104_bOutContactor | Frequency converter controlling pump R004-P-007 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TCV_107_wOutCommand | Temperature control valve - ext. supply cooling water | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TCV_118_wOutCommand | Temperature control valve - convertors cooling water | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TCV_119_wOutCommand | Temperature control valve - reactors cooling water | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_103_wInValue | Intermediate cooling water temperature upstream R004-W-005 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_105_wInValue | Ext. supply cooling water inlet temperature to heat exchanger R004-W-005 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_106_wInValue | Ext. supply cooling water outlet temperature from R004-W-005 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_107_wInValue | Intermediate cooling water temperature downstream R004-W-005 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_108_wInValue | Intermediate cooling water return temperature - reactors primary cooling | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_110_wInValue | Intermediate cooling water return temperature - convertors primary cooling | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R004_TT_121_wInValue | Intermediate cooling water return temperature - nitrogen gas treatment | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_FCV_122_wOutCommand | Flow control valve - Cooling water flow through purification system | AO_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_FIT_122_wInValue | Cooling water flow through water purification system R010 | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_PDS_151_bInInput | Differential pressure switch for police filter R010-F-101 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_PDT_152_wInValue | Differential pressure - pressure drop over ion exchangers | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_QT_150_wInValue | Conductivity transmitter for conductivity measurement of outgoing purified cooling water | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_TT_153_wInValue | Unpurified cooling water inlet temperature to purification system | AI_4-20mA | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_101_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_101_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_101_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_101_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_104_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_104_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_104_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_104_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_105_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_105_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_105_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_105_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_106_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_106_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_106_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_106_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_107_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_107_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_107_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_107_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_109_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_109_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_109_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_109_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_111_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_111_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_111_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_111_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_114_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_114_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_114_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_114_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_115_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_115_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_115_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_115_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_116_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_116_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_116_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_116_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_117_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_117_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_117_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_117_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_119_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_119_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_119_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R010_YSV_119_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | CC-Link-IE-Field | iQ-R | Section1
R011_FCV_222_wOutCommand | Flow control valve - Cooling water flow through purification system | AO_4-20mA | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_FIT_222_wInValue | Cooling water flow through water purification system R011 | AI_4-20mA | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_FIT_254_wInValue | Cleaning water flow and volume when cleaning the ion exchange vessels | AI_4-20mA | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_PDS_251_bInInput | Differential pressure switch for police filter R011-F-201 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_PDT_252_wInValue | Differential pressure - pressure drop over ion exchangers | AI_4-20mA | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_QT_250_wInValue | Conductivity transmitter for conductivity measurement of outgoing purified cooling water | AI_4-20mA | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_TT_253_wInValue | Unpurified cooling water inlet temperature to purification system | AI_4-20mA | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_201_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_201_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_201_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_201_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_204_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_204_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_204_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_204_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_205_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_205_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_205_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_205_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_206_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_206_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_206_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_206_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_207_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_207_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_207_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_207_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_209_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_209_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_209_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_209_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_211_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_211_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_211_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_211_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_214_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_214_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_214_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_214_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_215_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_215_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_215_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_215_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_216_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_216_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_216_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_216_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_217_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_217_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_217_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_217_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_219_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_219_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_219_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_219_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_224_bInSignalHome | Resin flush on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_224_bInSignalWork | Resin flush on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_224_bOutCommandHome | Resin flush on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R011_YSV_224_bOutCommandWork | Resin flush on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section1
R001_FCV_114_wOutCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FCV_124_wOutCommand | Flow control valve - Cooling water flow to lower reactor | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FCV_125_wOutCommand | Flow control valve - Cooling water flow to lower reactor | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FCV_129_wOutCommand | Flow control valve - Cooling water flow to upper reactor | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FCV_130_wOutCommand | Flow control valve - Cooling water flow to upper reactor | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FIT_124_wInValue | Flow transmitter for measuring primary cooling water flow to lower reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FIT_125_wInValue | Flow transmitter for measuring primary cooling water flow to lower reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FIT_129_wInValue | Flow transmitter for measuring primary cooling water flow to upper reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_FIT_130_wInValue | Flow transmitter for measuring primary cooling water flow to upper reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_LCV_102_wOutCommand | Control valve for deionized water inlet to storage vessel R001-B-001 | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_LSZ_116_bInInput | Level switch LowLow for storage vessel R001-B-001 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_LSZ_117_bInInput | Level switch HighHigh for storage vessel R001-B-001 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_LT_104_wInValue | Level transmitter for storage vessel R001-B-001 water level | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_PIT_103_wInValue | Pressure transmitter for storage vessel R001-B-001 pressure | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_PSA_002_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_TT_101_wInValue | Primary cooling water return temperature from upper reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_TT_102_wInValue | Primary cooling water return temperature from upper reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_TT_103_wInValue | Primary cooling water return temperature from lower reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_TT_104_wInValue | Primary cooling water return temperature from lower reactor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_TT_105_wInValue | Primary cooling water temperature upstream R001-W-001 | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_YSV_115_bInSignalHome | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_YSV_115_bInSignalWork | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_YSV_115_bOutCommandHome | Cooled objects isolation on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R001_YSV_115_bOutCommandWork | Cooled objects isolation on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_FCV_114_wOutCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_FCV_124_wOutCommand | Flow control valve - Cooling water flow to lower convertor | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_FCV_125_wOutCommand | Flow control valve - Cooling water flow to upper convertor | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_FIT_124_wInValue | Flow transmitter for measuring primary cooling water flow to lower convertor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_FIT_125_wInValue | Flow transmitter for measuring primary cooling water flow to upper convertor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_LCV_102_wOutCommand | Control valve for deionized water inlet to storage vessel R002-B-005 | AO_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_LSZ_116_bInInput | Level switch Low for storage vessel R002-B-005 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_LSZ_117_bInInput | Level switch High for storage vessel R002-B-005 | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_LT_104_wInValue | Level transmitter for storage vessel R002-B-005 water level | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_PIT_103_wInValue | Pressure transmitter for storage vessel R002-B-005 pressure | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_PSA_002_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_TT_105_wInValue | Primary cooling water temperature upstream R002-W-003 | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_TT_144_wInValue | Primary cooling water return temperature from upper convertor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_TT_145_wInValue | Primary cooling water return temperature from lower convertor | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_YSV_115_bInSignalHome | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_YSV_115_bInSignalWork | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_YSV_115_bOutCommandHome | Cooled objects isolation on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R002_YSV_115_bOutCommandWork | Cooled objects isolation on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R004_PSA_002_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R004_PT_102_wInValue | Pressure transmitter for vessel R004-B-011 level measurement | AI_4-20mA | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R004_YSV_101_bInSignalHome | Deionized water inlet on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R004_YSV_101_bInSignalWork | Deionized water inlet on-off valve | DI_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R004_YSV_101_bOutCommandHome | Deionized water inlet on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
R004_YSV_101_bOutCommandWork | Deionized water inlet on-off valve | DO_24VDC | Production_Line_2 | CC-Link-IE-Field | iQ-R | Section2
We recommend pasting data as "Values" in order to use data validation in this worksheet and to detect eventual errors in your data before you upload it to PLCCreator.
You can still use direct paste because the complete validation is performed in PLCCreator.
Don't forget to save this worksheet as csv file before you upload it to PLCCreator.

## data
Signal Type | Comm Protocol | Hardware Platform
AI_0-10VDC | CC-Link-IE-Field | ControlLogix
AI_0-20mA | EtherNet/IP | ET200M
AI_0-5VDC | Profibus | ET200MP
AI_-10-10VDC | Profinet | ET200Pro
AI_-1-1VDC | S7-300_Rack_Expansion | ET200SP
AI_1-5VDC | S7-400_Rack_Expansion | ET200SPHA
AI_-2.5-2.5VDC |  | iQ-R
AI_-20-20mA |  | S7-400
AI_-250-250mVDC
AI_-25-25mVDC
AI_4-20mA
AI_-500-500mVDC
AI_-50-50mVDC
AI_RTD-Ni-100
AI_RTD-Pt-100
AO_0-10VDC
AO_0-20mA
AO_-20-20mA
AO_4-20mA
DI_24VDC
DO_24VDC