## signals-template-type-12
Signals IO List Template Type | 12
Name | Description | Signal Type | Fieldbus | Comm Protocol | Hardware Platform | Group
R001_FIT_113_rInMeasurement | Flow transmitter for measuring primary cooling water flow in main loop | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_PIT_114_rInMeasurement | Pressure transmitter for cooling water pressure upstream cooled objects | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_PIT_118_rInMeasurement | Pressure transmitter measuring pressure after cooled objects | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_PSA_001_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_PSZ_101_bInInputActive | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_PSZ_102_bInInputActive | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_PSZ_103_bInInputActive | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_PSZ_104_bInInputActive | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_QIT_112_rInMeasurement | Conductivity transmitter for conductivity measurement in main cooling loop | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_001_bInContactorSwitch | Frequency converter controlling pump R001-P-001 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_001_bInMtrThrmProt | Frequency converter controlling pump R001-P-001 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_001_bInMtrFldSwitch | Frequency converter controlling pump R001-P-001 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_001_rInSpeedFeedback | Frequency converter controlling pump R001-P-001 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_001_rOutSpeedSetpoint | Frequency converter controlling pump R001-P-001 | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_002_bInContactorSwitch | Frequency converter controlling pump R001-P-002 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_002_bInMtrThrmProt | Frequency converter controlling pump R001-P-002 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_002_bInMtrFldSwitch | Frequency converter controlling pump R001-P-002 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_002_rInSpeedFeedback | Frequency converter controlling pump R001-P-002 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_SICA_002_rOutSpeedSetpoint | Frequency converter controlling pump R001-P-002 | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R001_TT_109_rInMeasurement | Primary cooling water temperature downstream R001-W-001 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_FIT_113_rInMeasurement | Flow transmitter for measuring primary cooling water flow in main loop | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_PIT_114_rInMeasurement | Pressure transmitter for cooling water pressure upstream cooled objects | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_PIT_118_rInMeasurement | Pressure transmitter measuring pressure after cooled objects | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_PSA_001_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_PSZ_101_bInInputActive | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_PSZ_102_bInInputActive | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_QIT_112_rInMeasurement | Conductivity transmitter for conductivity measurement in main cooling loop | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_005_bInContactorSwitch | Frequency converter controlling pump R002-P-005 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_005_bInMtrThrmProt | Frequency converter controlling pump R002-P-005 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_005_bInMtrFldSwitch | Frequency converter controlling pump R002-P-005 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_005_rInSpeedFeedback | Frequency converter controlling pump R002-P-005 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_005_rOutSpeedSetpoint | Frequency converter controlling pump R002-P-005 | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_006_bInContactorSwitch | Frequency converter controlling pump R002-P-006 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_006_bInMtrThrmProt | Frequency converter controlling pump R002-P-006 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_006_bInMtrFldSwitch | Frequency converter controlling pump R002-P-006 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_006_rInSpeedFeedback | Frequency converter controlling pump R002-P-006 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_SICA_006_rOutSpeedSetpoint | Frequency converter controlling pump R002-P-006 | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R002_TT_109_rInMeasurement | Primary cooling water temperature downstream R002-W-003 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_FCV_110_rInPositionFeedback | Flow control valve for minimum cooling water flow - by-pass valve | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_FCV_110_rOutPositionCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_PDT_106_rInMeasurement | Differential pressure transmitter for measuring intermediate cooling water flow to reactors primary cooling | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_PDT_107_rInMeasurement | Differential pressure transmitter for measuring intermediate cooling water flow to convertors primary cooling | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_PDT_110_rInMeasurement | Differential pressure transmitter for measuring intermediate cooling water flow | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_PDT_115_rInMeasurement | Differential pressure transmitter for measuring ext. supply cooling water flow | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_PDT_120_rInMeasurement | Differential pressure transmitter for measuring intermediate cooling water flow to nitrogen gas treatment | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_PSA_001_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R004_PT_104_rInMeasurement | Pressure transmitter measuring supply pressure to cooled objects | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_SICA_104_bInContactorSwitch | Frequency converter controlling pump R004-P-007 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R004_SICA_104_bInMtrThrmProt | Frequency converter controlling pump R004-P-007 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R004_SICA_104_bInMtrFldSwitch | Frequency converter controlling pump R004-P-007 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R004_SICA_104_rInSpeedFeedback | Frequency converter controlling pump R004-P-007 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_SICA_104_rOutSpeedSetpoint | Frequency converter controlling pump R004-P-007 | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TCV_107_rInPositionFeedback | Temperature control valve - ext. supply cooling water | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TCV_107_rOutPositionCommand | Temperature control valve - ext. supply cooling water | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TCV_118_rInPositionFeedback | Temperature control valve - convertors cooling water | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TCV_118_rOutPositionCommand | Temperature control valve - convertors cooling water | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TCV_119_rInPositionFeedback | Temperature control valve - reactors cooling water | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TCV_119_rOutPositionCommand | Temperature control valve - reactors cooling water | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_103_rInMeasurement | Intermediate cooling water temperature upstream R004-W-005 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_105_rInMeasurement | Ext. supply cooling water inlet temperature to heat exchanger R004-W-005 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_106_rInMeasurement | Ext. supply cooling water outlet temperature from R004-W-005 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_107_rInMeasurement | Intermediate cooling water temperature downstream R004-W-005 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_108_rInMeasurement | Intermediate cooling water return temperature - reactors primary cooling | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_110_rInMeasurement | Intermediate cooling water return temperature - convertors primary cooling | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R004_TT_121_rInMeasurement | Intermediate cooling water return temperature - nitrogen gas treatment | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_FCV_122_rInPositionFeedback | Flow control valve - Cooling water flow through purification system | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_FCV_122_rOutPositionCommand | Flow control valve - Cooling water flow through purification system | AO_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_FIT_122_rInMeasurement | Cooling water flow through water purification system R010 | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_PDS_151_bInInputActive | Differential pressure switch for police filter R010-F-101 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_PDT_152_rInMeasurement | Differential pressure - pressure drop over ion exchangers | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_PSA_001_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_QT_150_rInMeasurement | Conductivity transmitter for conductivity measurement of outgoing purified cooling water | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_TT_153_rInMeasurement | Unpurified cooling water inlet temperature to purification system | AI_4-20mA | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_101_bInStatusClosed | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_101_bInStatusOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_101_bOutCommandOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_104_bInStatusClosed | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_104_bInStatusOpen | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_104_bOutCommandOpen | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_105_bInStatusClosed | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_105_bInStatusOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_105_bOutCommandOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_106_bInStatusClosed | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_106_bInStatusOpen | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_106_bOutCommandOpen | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_107_bInStatusClosed | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_107_bInStatusOpen | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_107_bOutCommandOpen | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_109_bInStatusClosed | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_109_bInStatusOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_109_bOutCommandOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_111_bInStatusClosed | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_111_bInStatusOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_111_bOutCommandOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_114_bInStatusClosed | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_114_bInStatusOpen | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_114_bOutCommandOpen | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_115_bInStatusClosed | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_115_bInStatusOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_115_bOutCommandOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_116_bInStatusClosed | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_116_bInStatusOpen | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_116_bOutCommandOpen | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_117_bInStatusClosed | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_117_bInStatusOpen | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_117_bOutCommandOpen | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_119_bInStatusClosed | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_119_bInStatusOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R010_YSV_119_bOutCommandOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | f1 | EtherNet/IP | ControlLogix | Section1
R011_FCV_222_rInPositionFeedback | Flow control valve - Cooling water flow through purification system | AI_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_FCV_222_rOutPositionCommand | Flow control valve - Cooling water flow through purification system | AO_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_FIT_222_rInMeasurement | Cooling water flow through water purification system R011 | AI_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_FIT_254_rInMeasurement | Cleaning water flow and volume when cleaning the ion exchange vessels | AI_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_PDS_251_bInInputActive | Differential pressure switch for police filter R011-F-201 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_PDT_252_rInMeasurement | Differential pressure - pressure drop over ion exchangers | AI_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_PSA_001_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_QT_250_rInMeasurement | Conductivity transmitter for conductivity measurement of outgoing purified cooling water | AI_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_TT_253_rInMeasurement | Unpurified cooling water inlet temperature to purification system | AI_4-20mA | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_201_bInStatusClosed | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_201_bInStatusOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_201_bOutCommandOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_204_bInStatusClosed | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_204_bInStatusOpen | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_204_bOutCommandOpen | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_205_bInStatusClosed | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_205_bInStatusOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_205_bOutCommandOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_206_bInStatusClosed | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_206_bInStatusOpen | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_206_bOutCommandOpen | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_207_bInStatusClosed | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_207_bInStatusOpen | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_207_bOutCommandOpen | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_209_bInStatusClosed | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_209_bInStatusOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_209_bOutCommandOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_211_bInStatusClosed | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_211_bInStatusOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_211_bOutCommandOpen | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_214_bInStatusClosed | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_214_bInStatusOpen | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_214_bOutCommandOpen | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_215_bInStatusClosed | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_215_bInStatusOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_215_bOutCommandOpen | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_216_bInStatusClosed | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_216_bInStatusOpen | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_216_bOutCommandOpen | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_217_bInStatusClosed | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_217_bInStatusOpen | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_217_bOutCommandOpen | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_219_bInStatusClosed | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_219_bInStatusOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_219_bOutCommandOpen | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_224_bInStatusClosed | Resin flush on-off valve | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_224_bInStatusOpen | Resin flush on-off valve | DI_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R011_YSV_224_bOutCommandOpen | Resin flush on-off valve | DO_24VDC | Production_Line_1 | EtherNet/IP | ControlLogix | Section1
R001_FCV_114_rInPositionFeedback | Flow control valve for minimum cooling water flow - by-pass valve | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_114_rOutPositionCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_124_rInPositionFeedback | Flow control valve - Cooling water flow to lower reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_124_rOutPositionCommand | Flow control valve - Cooling water flow to lower reactor | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_125_rInPositionFeedback | Flow control valve - Cooling water flow to lower reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_125_rOutPositionCommand | Flow control valve - Cooling water flow to lower reactor | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_129_rInPositionFeedback | Flow control valve - Cooling water flow to upper reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_129_rOutPositionCommand | Flow control valve - Cooling water flow to upper reactor | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_130_rInPositionFeedback | Flow control valve - Cooling water flow to upper reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FCV_130_rOutPositionCommand | Flow control valve - Cooling water flow to upper reactor | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FIT_124_rInMeasurement | Flow transmitter for measuring primary cooling water flow to lower reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FIT_125_rInMeasurement | Flow transmitter for measuring primary cooling water flow to lower reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FIT_129_rInMeasurement | Flow transmitter for measuring primary cooling water flow to upper reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_FIT_130_rInMeasurement | Flow transmitter for measuring primary cooling water flow to upper reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_LCV_102_rInPositionFeedback | Control valve for deionized water inlet to storage vessel R001-B-001 | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_LCV_102_rOutPositionCommand | Control valve for deionized water inlet to storage vessel R001-B-001 | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_LSZ_116_bInInputActive | Level switch LowLow for storage vessel R001-B-001 | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_LSZ_117_bInInputActive | Level switch HighHigh for storage vessel R001-B-001 | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_LT_104_rInMeasurement | Level transmitter for storage vessel R001-B-001 water level | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_PIT_103_rInMeasurement | Pressure transmitter for storage vessel R001-B-001 pressure | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_PSA_002_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_TT_101_rInMeasurement | Primary cooling water return temperature from upper reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_TT_102_rInMeasurement | Primary cooling water return temperature from upper reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_TT_103_rInMeasurement | Primary cooling water return temperature from lower reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_TT_104_rInMeasurement | Primary cooling water return temperature from lower reactor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_TT_105_rInMeasurement | Primary cooling water temperature upstream R001-W-001 | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_YSV_115_bInStatusClosed | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_YSV_115_bInStatusOpen | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R001_YSV_115_bOutCommandOpen | Cooled objects isolation on-off valve | DO_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FCV_114_rInPositionFeedback | Flow control valve for minimum cooling water flow - by-pass valve | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FCV_114_rOutPositionCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FCV_124_rInPositionFeedback | Flow control valve - Cooling water flow to lower convertor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FCV_124_rOutPositionCommand | Flow control valve - Cooling water flow to lower convertor | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FCV_125_rInPositionFeedback | Flow control valve - Cooling water flow to upper convertor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FCV_125_rOutPositionCommand | Flow control valve - Cooling water flow to upper convertor | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FIT_124_rInMeasurement | Flow transmitter for measuring primary cooling water flow to lower convertor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_FIT_125_rInMeasurement | Flow transmitter for measuring primary cooling water flow to upper convertor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_LCV_102_rInPositionFeedback | Control valve for deionized water inlet to storage vessel R002-B-005 | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_LCV_102_rOutPositionCommand | Control valve for deionized water inlet to storage vessel R002-B-005 | AO_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_LSZ_116_bInInputActive | Level switch Low for storage vessel R002-B-005 | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_LSZ_117_bInInputActive | Level switch High for storage vessel R002-B-005 | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_LT_104_rInMeasurement | Level transmitter for storage vessel R002-B-005 water level | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_PIT_103_rInMeasurement | Pressure transmitter for storage vessel R002-B-005 pressure | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_PSA_002_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_TT_105_rInMeasurement | Primary cooling water temperature upstream R002-W-003 | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_TT_144_rInMeasurement | Primary cooling water return temperature from upper convertor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_TT_145_rInMeasurement | Primary cooling water return temperature from lower convertor | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_YSV_115_bInStatusClosed | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_YSV_115_bInStatusOpen | Cooled objects isolation on-off valve | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R002_YSV_115_bOutCommandOpen | Cooled objects isolation on-off valve | DO_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R004_PSA_002_bInInputActive | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R004_PT_102_rInMeasurement | Pressure transmitter for vessel R004-B-011 level measurement | AI_4-20mA | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R004_YSV_101_bInStatusClosed | Deionized water inlet on-off valve | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R004_YSV_101_bInStatusOpen | Deionized water inlet on-off valve | DI_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
R004_YSV_101_bOutCommandOpen | Deionized water inlet on-off valve | DO_24VDC | Production_Line_2 | EtherNet/IP | ControlLogix | Section2
We recommend pasting data as "Values" in order to use data validation in this worksheet and to detect eventual errors in your data before you upload it to PLCCreator.
You can still use direct paste because the complete validation is performed in PLCCreator.
Don't forget to save this worksheet as csv file before you upload it to PLCCreator.

## data
Signal Type | Comm Protocol | Hardware Platform
AI_0-10VDC | CC-Link-IE-Field | ControlLogix
AI_0-20mA | EtherNet/IP | ET200M
AI_0-5VDC | Profibus | ET200MP
AI_-10-10VDC | Profinet | ET200Pro
AI_-1-1VDC | S7-300_Rack_Expansion | ET200SP
AI_1-5VDC | S7-400_Rack_Expansion | ET200SPHA
AI_-2.5-2.5VDC |  | iQ-R
AI_-20-20mA |  | S7-400
AI_-250-250mVDC
AI_-25-25mVDC
AI_4-20mA
AI_-500-500mVDC
AI_-50-50mVDC
AI_RTD-Ni-100
AI_RTD-Pt-100
AO_0-10VDC
AO_0-20mA
AO_-20-20mA
AO_4-20mA
DI_24VDC
DO_24VDC